## Development
Project Name: Arecibo Observatory
Project Engineer Vinod Sivan
IDC Engineer: Agasti
US Software Engineer: Fernando
| Closed | Question/Issue | Date | Resolution | Date
1 | X | Operation of F1 and F2 | 2010-05-27 | F1 and F2 should be outside the scope of LA/LS. Custom Logic will need to be written for F1 and F2. F1 should have a HMI input for Min gens online. F2 should only close when in "Operation with transmitters" mode. | 2010-05-27
2 | X | Operation of "Operation with Transmitters" mode. | 2010-05-27 | If F2 is closed, F1 requires all generators to be online in order to close. F1 really is acting like a generator main breaker and it would be advisable to use system type 7 as a starting point. Using type 7 will adjust the LA/LS to accommodate for F1 being used as a GM breaker. If Utility Returns after a failure in "Operation with Transmitters" mode, F1 should re-open and gen that is not selected for use in "Operation with Transmitters" mode should shut down. | 2010-05-27
3 | X | Operation of F1 and F2 Under Bus Overload Condition | 2010-06-04 | No, we don’t have to define the operation under bus overload conditions. | 2010-06-04
4 | X | Do we need to have standard LA/LS Setting entry fields on "System Control Screen" | 2010-06-04 | Yes. Leave it on the screen. | 2010-06-04
5 | X | Functional Test forms are not In-line with SOP, In SOP it's mentioned that 52-F1 CB will act like a GM Breaker and is Normally open type, But in Functional Test forms it mentioned as a Normally closed type. | 2010-06-20 | The original SOP was not correct (ver. A & B). The functional test form is correct; also the SOP of version C & D have been updated. | 2010-06-27
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42

## Peer Review - U.S.
| Question/Issue/Change | Date | Resolution/Change | Date
1 | The original SOP that you used to develop the program has been updated to reflect the Functional Test Forms; so for these changes please use SOP version D. On Page 1 under Normal Conditions, the new SOP ver.D states: The generator breakers 52-G1 through 52-G4, feeder breakers 52-F2 is open and 52-F1 is closed. Please change the program to relfect this new change and make 52-F1 a normally closed breaker. Good job following the original SOP, unfortunately it changed. | 2010-07-27 | feeder breakers 52-F1 is closed in Normal conditions, this means at starting of system this breaker should be closed by any mean and PLC should receive "A" position for that breaker. So Breaker must be closed manually at startup. We can't program normal condition, this are conditions required to start the system. For simulation purpose you can follow following sequence to close 52-F1 at start up. 1. Turn ON "Operations with Transmitters". 2. Fail Utility/give signal "HWI_System_Run_Start". | 2010-07-28
2 | On Page 1 under Normal Load Control the SOP states: The highest priority load add level is level 1, which adds when the first genset comes online. Additional add levels come online as the remaining gensets parallel and close to the emergency bus. For example, when the second genset closes to the emergency bus, load add level 2 is picked up. Currently what happens is that as soon as the gensets are on-line and 52-F1 is open, the Load Shed signals become active in the program and the the Load add never becomes active. The LA/LS sequence is not working. Please correct. NOTE: Once you resove issue number 1 above this issue also gets resolved. | 2010-07-27 | See Note for Issue No.1 | 2010-07-28
3 | The Load demand does not work. When I simulate a utility failure and setup the following parameters in the System Control Screen nothing happens (gensets do not shutdown). Additionally. LA/LS does not work in Test with Load. NOTE: Once you resove issue number 1 above this issue also gets resolved. | 2010-07-27 | See Note for Issue No.1 | 2010-07-28
4 | The original SOP that you used to develop the program has been updated to reflect the Functional Test Forms; so for these changes please use SOP version D. On Page 4 under Operation with Transmitters, the new SOP ver.D states: If normal power fails during operation with transmitters, 52-F1 opens. The fourth genset automatically would start, parallel and close to the bus. After all the gensets are online, 52-F1 closes. If a bus overload is sensed under these conditions, 52-F2 opens and system is taken out of ‘Transmitter Operation’. This sequence does not occur, please correct. | 2010-07-27 | Changes done as per new SOP Ver. D and tested as per new Functional test forms | 2010-07-28
5 | On Page 4 under Manual Mode from the PowerCommand Control (PCC) the SOP states: Before starting the gensets and connecting them to the emergency bus, shed noncritical and high-inrush feeder breaker loads by pressing the Open button on the front of each feeder breaker. By noncritical and high-inrush feeder breaker loads this means shed 52-F1. So please put an Open and Close button next to 52-F1 in order to manually control 52-F1 in both Auto and Manual modes. Also note that by adding this button we resolve issue number 1 above. Please put a security level of 1 or greater on these buttons. | 2010-07-28 | Changes done as per requirement.
6 | On Page 4 under Operation with Transmitters the SOP states: If Load Demand Mode is on, the MasterControl monitors the system load and operates as described in Load Demand Mode. Also in the Functional test form under Operations with Transmitters - NSF it states: -Reduce the load to zero -Verify the fourth genset shuts down on load demand -Verify other generators keep running and do not shut down on load demand What happens if the load increases to 80% is that Gen 4 in this case will start, then 52-F1 will Open, then G4 will go on-line, then 52-F1 will close again. In this case 52-F1 should not open again when Gen 4 comes on-line because it is in load demand. Please correct. | 2010-07-28 | Changes done as per requirement.
7 | Also if 52-F2 fails to close when the system is put in Transmitter mode, we should abort Transmitter mode and annunciate a Fault. | 2010-07-28 | Changes done as per requirement.
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42

## Test Phase
| Question/Issue/Change | Date | Resolution/Change | Date
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42