ARECIBO OBSERVATORY

SERVO DRIVE SYSTEM UPGRADE

Volume II - Section 4

OPERATION AND MAINTENANCE MANUAL

CONTROL SYSTEMS


Modifications And Adjustments

Provided for

National Astronomy and Ionosphere Center
Cornell University

Ithaca, NY, USA

Project No. 10/95034
Rev.: 2.3
December 1999

| Vertex Antennentechnik GmbH Baumstr. 50 47198 Duisburg Germany Tel. +49-2066-2096-0; Fax -11 |  |
| --- | --- |

This part of the O&M manual describes modifications and adjustments of various off-the-shelf components which are necessary to use this equipment for the Arecibo Servo Drive System.

The numbers of the paragraphs refer to the related sections of Vol. IV (O&M Manual Control Systems, Part "Vendor Publications").

Table of Contents

Page 4 - ...

1. PROGRAMMABLE CONTROLLER SIEMENS S5-135U

1.1. General

1.2. CPU 928B

1.3. Plug-In PC CP 581

1.3.1. Hardware

1.3.2. Software:

1.3.2.1. Setup

1.3.2.2. Software on Onboard Silicon Disk

1.4. Serial Interface CP 524

1.5. Position Measuring Module WF 705

1.6. Ethernet Interface Module

1.7. Time Code Reader

1.8. Input And Output Modules

1.8.1. Address Selection (All Modules)

1.8.2. Enable Jumpers (All Modules)

1.8.3. Digital Input And Output Modules

1.8.4. Analog Input Modules

1.8.5. Analog Output Modules

2. KOLLMORGEN BRUSHLESS DRIVE AMPLIFIERS BDS 4A

2.1. Power Supply Module PSR4

2.2. Amplifier BDS4A

2.3. Maccon Regeneration Module TWN 34

3. TR OPTICAL ENCODERS CE-65

3.1. Parameters

3.2. Encoder Calibration

4. VERTEX PORTABLE CONTROL UNIT

5. LIMIT SWITCHES

5.1. Schmersal Rotary Cam Switches

5.2. Schmersal Mechanical Limit Switches

6. VERTEX DRIVE CONTROL SYSTEM

6.1. Drive Control System Azimuth

6.1.1. Nominal Velocity Board 295.4

6.1.2. Actual Velocity Board 329.3

6.1.2.1. Components

6.1.2.2. Tacho Adjustment

6.1.2.3. Adjustment of Zero Speed Threshold

6.1.3. Speed Controller Board 334.3

6.1.3.1. Components

6.1.3.2. Bias torque adjustment

6.1.4. Universal Amplifier Board 421.0

6.1.4.1. Components

6.2. Drive Control System Gregorian Dome

6.2.1. Nominal Velocity Board 295.4

6.2.2. Actual Velocity Board 329.3

6.2.2.1. Components

6.2.2.2. Tacho Adjustment

6.2.2.3. Adjustment of Zero Speed Threshold

6.2.3. Speed Controller Board 334.3

6.2.3.1. Components

6.2.3.2. Torque Bias Adjustment

6.2.4. Universal Amplifier Board 421.0

6.2.4.1. Components

6.3. Drive Control System Carriage House

6.3.1. Nominal Velocity Board 295.4

6.3.2. Actual Velocity Board 329.3

6.3.2.1. Components

6.3.2.2. Tacho Adjustment

6.3.2.3. Adjustment of Zero Speed Threshold

6.3.3. Speed Controller Board 334.3

6.3.3.1. Components

6.3.3.2. Torque Bias Adjustment

7. UNINTERRUPTABLE POWER SUPPLY

8. SWITCHGEAR INSIDE DRIVE CABINET

8.1. Voltage Supervision Relay Dold BA 9054

8.2. Current Supervision Relay Pilz P1IK

8.3 Schiele Overvoltage Protection Relay

Updates

Version 2.1 - Aug 97

| page | paragraph | subject | modification |
| --- | --- | --- | --- |
| 18 | 5.1 | limits | prelimit distance |

Version 2.2 - Sept 97

| page | paragraph | subject | modification |
| --- | --- | --- | --- |
| 36 | 6.2.4.1 | components DCS | GD board 13A1, R503 changed |

Version 2.3 - Dec 99

| page | paragraph | subject | modification |
| --- | --- | --- | --- |
| 28 | 6.1.4.1 | components DCS | Az board 13A1/14A1, R *04 changed |
| 40 | 6.3.3.1 | components DCS | CH board 11A1, R 45 changed |

# 1.	Programmable Controller Siemens S5-135U

## 1.1.	General

Switches At PLC Front

The switches listed below are located at the front side of the PLC.

| Designation | Location | Function | required position |
| --- | --- | --- | --- |

───────────────────────────────────────────────────────────────

| Voltage Selector RUN/STOP RESET/OVERALL RESET RUN/STOP RUN/STOP | Power Supply Unit CPU 928B CPU 928B CP581 CP524 | Selection 115V/230V mode selection CPU reset mode selection mode selection | local mains voltage RUN neutral position RUN RUN |
| --- | --- | --- | --- |

## 1.2.	CPU 928B

No adjustments required

## 1.3.	Plug-In PC CP 581

### 1.3.1.	Hardware

Setting of Jumpers:

┌──┬──────────────────────────────────────────────┐
└──┤                                              │
   │                                              │
   ├────────────────────┐                         │
   │                    │                         │
   │                    │                         │
   │  Memory Card Slot  │                         │
   │                    │         ░               │
   │                    │         ░ X44           │
   ├────────────────────┘                         │
   │                   ▄▄                         │
   │               X30 ▄▄                         │
   │                                              │
   │                3█                            │
   │                2█  X43                       │
   │                1_                            │
   │                                              │
   │                1_                            │
   │       123      2█  X55                       │
   │ ▄ ▄   _██      3█                            │
   │ █ █                                          │
   │X51    X40                                    │
   │  X50                                         │
   │                                              │
   │ ░                                            │
   │ ░  ░                                         │
   │ X3 ░                                         │
   │    X5                                        │
   │                                   X41        │
   │                                  ┌───┐       │
   │                                  │   │       │
   │                                  │██ │       │
┌──┤                                  └───┘       │
└──┴──────────────────────────────────────────────┘

░ : jumper not inserted

Attention!

The CP581 used for the Arecibo PLC has to be equipped with a Math Coprocessor 80387. An 80387 chip will be installed on each CP581 supplied for this project by Vertex.

When purchasing a CP581 directly from Siemens make sure that the 80387 option is included (Siemens Order No. 6ES5 581-0KA11).

### 1.3.2.	Software:

#### 1.3.2.1.	Setup

The CP 581 are set up for booting from the onboard silicon disc. The setup of the CP 581 has been modified accordingly. In normal operation, during power down times and even after unplugging the whole module the stored setup will be kept. No adjustments are necessary.

Deviations from standard setup:

Drive A	None
Drive B	None
Parameter "Boot Sequence":	C, A
Parameter "Auto Detect IDE":	Disabled
Parameter "Drive C":	OSD
Parameter "Drive D":	None

The setup can be entered after powering up the CP581 or after a software restart (use "RES" pushbutton on CP581 front panel) and follow instructions on the monitor.

To modify the setup the LCU monitor and a keyboard have to be connected to the CP 581.

Attention!

If a CP581 is purchased directly from Siemens, the OSD must be formatted and set up for booting before being able to download the application software.
This procedure can be found Siemens CP581 manual,
 file 1 (hardware), par. 2.10.2.
Observe that a mass storage device is definitely required 
(e.g. HD/FDD unit, Siemens order no. 6ES5 581-1LA11)!

#### 1.3.2.2.	Software on Onboard Silicon Disk

Warning!

Modifications of the OSD software require some knowledge of PC handling, e.g. DOS commands, editors etc.

Any modifications should be done by experienced personnel only!

The Onboard Silicon Disk (OSD) is loaded with all necessary software. The Arecibo Servo & Drive application software will be started automatically in file Autoexec.bat.

## 1.4.	Serial Interface CP 524

Jumpers on CP 524:

┌──┬──────────────────────────────────────────────┐
└──┤        321                      16           │
   │        _██ Ju. 10                ┌────────┐  │
   ├────────────────────┐             │  J52   │  │
   │                    │             └────────┘  │
   │                    │             1           │
   │  EPROM - Slot      │            1            │
   │                    │   ┌────────┐            │
   │                    │   │  J54   │            │
   ├────────────────────┘   └────────┘            │
   │            1_                   16           │
   │     Ju.8   2█                                │
   │            3█                                │
   │                                              │
   │            1_                                │
   │     Ju.9   2█                              1 │
   │            3█                       ┌──────┐ │
   │            ┌─┐                      │ J53  │ │
   │            │#│                      └──────┘ │
   │            │#│                             16│
   │            └─┘                               │
   │            ██_ Ju.5                          │
   │            123           321                 │
   │      123                 _██  Ju.1           │
   │      ██_ Ju. 2                               │
   ├────────────────────┐                         │
   │                    │                         │
   │     Interface      │     123                 │
   │                    │     _██  Ju.7           │
   │      module        │     321                 │
   │                    │     _██  Ju.6           │
   ├────────────────────┘     123                 │
┌──┤                          _██  Ju.4           │
└──┴──────────────────────────────────────────────┘

Jumper Settings:

Jumper #	function	setting
───────────────────────────────────────────────────────────────
J52	IPC flags	all jumpers inserted

J53	address	addess 0  =  no jumper inserted

J54	system	jumpers 5-12 and 8-9 open,
		all others inserted

##	Test	all jumpers inserted

Jumpers 1 thru 10 are required for factory maintenance purposes only and should not be touched by the user.

Interface module 6ES5 752-0AA12:
(TTY interface)

Settings on the interface module:

┌─────────────────────────┐
│ front connector 25 pol. │
├─────────────────────────┤
│                         │
│                         │
│                         │
│   ██_ Ju. 3             │
│   321                   │
│                         │
│                         │
│                         │
│                         │
│                         │
│                         │
│                         │
│      Jumper #           │
│      4    2    1        │
│                         │
│     1█   1█   1_        │
│     2█   2█   2█        │
│     3_   3_   3█        │
│                         │
│                         │
├─────────────────────────┤
│     base connector      │
└─────────────────────────┘

This setting is the factory setting of Siemens.

Meaning of the settings:

-	Ju 1:	transmitted data with normal polarity

-	Ju 2:	received data with normal polarity

-	Ju 3:	current loop generation internally

-	Ju 4:	receive clock pulse from transmit pulse

## 1.5.	Position Measuring Module WF 705

┌──┬──────────────────────────────────────────────┐
└──┤                                    X9        │
   │                                    ██        │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                              │
   │                                       S1     │
   │                                      ┌───┐   │
   │                                 (MSB)│X  │8  │
   │                                      │X  │   │
   │                                      │  X│   │
   │                                      │X  │   │
   │                                      │X  │   │
   │                                      │X  │   │
   │                                      │  X│   │
   │                                 (LSB)│  X│1  │
   │                                      └───┘   │
   │                                    open clos.│
   │                              (selected)      │
   │       ██                                     │
   │       X7                                     │
   │                                              │
   │                                              │
   │    ░                                         │
┌──┤    X8                                        │
└──┴──────────────────────────────────────────────┘

░: jumper not inserted

Jumper Settings:

Jumper #	function	setting
───────────────────────────────────────────────────────────────
S1	address	Adress 220:
		switches 3,4,5,7,8 = on

X7	ground	inserted
		(external grounds of 5V and 24V connected)

X8	screen	off
		(screen connected to 5V DC ground)

Jumper X9 is required for factory maintenance purposes only and should not be touched by the user.

## 1.6.	Ethernet Interface Module

The Ethernet interface module is mounted to the first slot module of the CP581.

On the Ethernet module no adjustments are required.

## 1.7.	Time Code Reader

The IRIG-B Time Code Reader  module is mounted to the second slot module of the CP581.

The only necessary hardware setting is the module base address.

┌───────────────────────────────────────┐
      ┌───────┘                                       │
      │                                               │
      │                                               ├─┐
      │                                               │ │
      │                                               │ │
      │                                               │ │
      │                                               ├─┘
      │  1      6                                     │
      │  ┌──────┐                                     │
      │  │      │ SW1                                 ├──┐
      │  └──────┘                                     ├──┘
      └┐           ┌─┐                           ┌────┤
       └───────────┘ └───────────────────────────┘    │
                                                      │

Dip Switch Settings:

Switch #	function	setting
───────────────────────────────────────────────────────────────
SW1	address	Adress 200H:
		switches 2,3,4,5,6 = on

## 1.8.	Input And Output Modules

### 1.8.1.	Address Selection (All Modules)

When exchanging digital or analog input/output modules, the basic address must be set accordingly. Each module has its individual address (with both input and output modules beginning at zero).

The DIP switch for address selection is located at the side of each module.

The location of the modules in the PLC and their base addresses can be found in section 1 of this manual ("System Description“), par. 1.2.1.

Example:

Module No. +PLC-19D01
Digital Input Module
Base address: 12

┌───┬───┬───┬───┬───┬───┬───┬───┐
	│   │   │   │   │   │   │   │   │
  * = set to "ON"	│   │   │   │   │ * │ * │   │   │
	└───┴───┴───┴───┴───┴───┴───┴───┘
address value	 128  64  32  16  8   4   2   1

### 1.8.2.	Enable Jumpers (All Modules)

Each input and output module has an "enable" jumper on its (narrow) top side. If this jumper is plugged in, the module can (and must) be electrically enabled/disabled by applying resp. voltages to the +F/-F lines.

This function is not used for this application.

The enable jumper must be removed.

### 1.8.3.	Digital Input And Output Modules

Only address has to be set (see above).

### 1.8.4.	Analog Input Modules

The switches on the analog input module, Siemens type 6ES5 465-4UA12, must be set as follows:

Switch #1:

┌───┬───┬───┬───┬───┬───┬───┬───┐
	│   │   │   │ * │   │   │ * │   │
  	│ * │ * │ * │   │ * │ * │   │   │
	└───┴───┴───┴───┴───┴───┴───┴───┘
           |   |   |   |   -----   |   |
           |   |   |   |     |     |   |---	irrelevant        
           |   |   |   |     |     |-------	voltage measurement
           |   |   |   |     |-------------	no broken wire detection
           |   |   |   |-------------------	two's complement
           |   |   |-----------------------	16 channels
           |   |---------------------------	60 Hz
           |-------------------------------	cyclic measurements

Switch #2:

┌───┬───┬───┬───┬───┬───┬───┬───┐
	│ * │   │   │   │ * │ * │   │   │
  	│   │ * │ * │ * │   │   │ * │ * │
	└───┴───┴───┴───┴───┴───┴───┴───┘
           |   ----------  --------------
           |       |               |           
           |       |               |-------	16 channels mV/mAt
           |       |-----------------------	range 500 mV
           |-------------------------------	without compensation

The analog input modules have to be equipped with four measuring range modules ±10V (Siemens order no. 6ES5 498-1AA31).

### 1.8.5.	Analog Output Modules

Only address has to be set (cf. page 4-9).

# 2.	Kollmorgen Brushless Drive Amplifiers BDS 4A

## 2.1.	Power Supply Module PSR4

No adjustments required.

## 2.2.	Amplifier BDS4A

For the Kollmorgen amplifiers there is no adjustment necessary as part of any maintenance or calibration procedure. Once set up, the amplifiers can be used for any motor of the same axis. In addition to this, Gregorian Dome amplifiers may also be used for Carriage House drives and vice versa.

Purchase of a new amplifier

If a new amplifier is purchased from the manufacturer, please note that the motor type has to be specified when ordering the amplifier. Each amplifier will be prepared for a particular motor type at the factory. So the amplifiers for azimuth on one side and Gregorian Dome/Carriage House on the other side are of the same type but with different factory settings. They must not be exchanged!

In addition to this the amplifier have to be set up for torque input.

Any new amplifier has to be adjusted as follows:

Potentiometer s ettings:

-	Stability	fully ccw

-	Current limit	Az:	fully cw
	GD, CH:	"2 o'clock position"
		(with the letters on the pot being the bottom of 
		 the „clock“)

-	Command Scale	fully cw

-	Balance	N/A

Compensation Board

The compensation board contains all the settings which determine velocity or torque control, current and velocity loop gains etc.

The compensation board is located inside the amplifier and is mounted as a piggy-back module to the main board. For exchange of the compensation board the amplifier chassis must be opened.

| Component R4 R6 R7 R8 R9 R10 R13 R15 R23 R24 R25 R27 R28 R29 R32 C1 C2 C3 C12 C14 C16 C22 C26 C30 C31 C33 C35 C36 J11 J17 J18 J19 J20 J21 | Value 1.62 k 20k 3.9 k 3.65 k 16.2 k 20k 390k 390k 0 (bridge installed) factory setting factory setting factory setting open open closed open open closed |
| --- | --- |

A circuit diagram is shown in the Kollmorgen amplifier documentation, page F-55.

## 2.3.	Maccon Regeneration Module TWN 34

All nine regeneration modules used in the servo drive system are identical. The only adjustment that can be done with the regeneration modules is the setting of the switch-on threshold, which has been set to 350 Volts.

This value should not be modified since all voltage levels of the power supply and regeneration system are adapted to each other. A spare regeneration module should be ordered from the manufacturer with the required setting.

If for any reason a readjustment is necessary proceed as follows:

1.	The module should be adjusted "offline". Therefore take out module from regeneration rack.

2.	Connect a DC voltage supply to the incoming terminals of the module.

3.	Connect a voltmeter between TP3 and GND.

4.	Set the DC voltage supply to 350 V.

5.	Turn P1 (the only potentiometer on the regeneration module) ccw until the reading of the voltmeter is approx. 0.2 V.

6.	Turn P1 cw until the reading of the voltmeter changes to approx. 6 V.

# 3.	TR Optical Encoders CE-65

## 3.1.	Parameters

The TR encoders are programmable, i.e. parameters like steps per revolution, output code etc. can be entered electrically from outside. Once this has been done the encoders do not loose their setting. All parameters are internally stored in an EEPROM.

No modification or adjustment of parameters is required.

The positive sense of direction can be changed by connecting terminal 10 of the upper terminal block of the encoder interface module PT-15-2 to +24V or to 0V.

The standard setting is as follows:

Axis	Label of interface 	terminal 10	when rotated clockwise,
	module	connected to	encoder is counting
───────────────────────────────────────────────────────
Az 1	+Az-22D02	+24V	up
Az 2	+Az-23D02	+24V	up
GD	+GD-22D02	+24V	up
CH	+CH-22D02	+24V	up

The spare encoder supplied with the servo & drive system has already been loaded with the correct parameters. If a new encoder is purchased from the manufacturer, the specific parameters (see list below) can be specified and loaded at the factory. If for any reason parameters have to be modified later, this can be done by connecting a TR hand held pogramming device "Pt100" to the encoder interface units in the drive cabinet. Make sure that a Pt100 for CE type encoders is used.

In such a case, the parameters to be entered by the Pt100 into the encoder are as follows:

parametersetting	value	irrelevant?

───────────────────────────────────────────────────────
data format	SSI	
tree	yes
progr. gearing	no
measuring length [revolutions]	4096
measuring length [steps]	16777216
cw counting	up
offset	no
measuring start	0
preset input	rising ramp
1st preset value	6000000
2nd preset value	0	*
start safety range 	1	*
start operating range	1	*
end safety range 	1	*
end operating range	1	*
Code	Gray
SSI repeated	no
no.of position bits	24
1st special bit	0
2nd special bit	0	*
3rd special bit	0	*
4th special bit	0	*
5th special bit	0	*
6th special bit	0	*
display format	without comma	*
position display	no change	*
counter display	no change	*
TA: measuring length [steps]	16777216	*
TA: measuring start	0	*

Parameters marked with * are irrelevant anyway.

## 3.2.	Encoder Calibration

The PRESET procedure has to be performed after replacement or dismounting/remounting of an encoder.

Warning!

Since the encoder preset value (see parameterlist above) is fixed in the encoder, an encoder reset may only be performed in the agreed PRESET position, see list below!

It should be possible to locate these positions without using the encoders, e.g. by marks on the rack gear etc.

The PRESET procedure for a particular axis is as follows:

1.	Move axis to the physical encoder preset position.

2.	Select "Local Only" mode for the desires axis at the drive cabinet door.

3.	Activate LCU mode.

4.	Select axis.

5.	Press "F7" (Control).

6.	Press "F6" (Encoder Preset)

7.	Enter Password.

8.	Press "Reset" pushbutton at the drive cabinet.

9.	Position display at LCU should now show the Preset position. 
Please observe that any actual encoder correction will be added to the Preset position.

Preset Positions:

Azimuth	360.000 degr
Gregorian Dome	8.3851 degr
Carriage House	(tbd) degr

# 4.	Vertex Portable Control Unit

No adjustments required

# 5.	Limit Switches

## 5.1.	Schmersal Rotary Cam Switches

The rotary cam switches for Gregorian Dome and/or Carriage House have to be readjusted

-	after exchanging the cam switch / encoder assembly

-	after exchanging the cam switch

-	after modifying the actual (mechanical) travel range.

The readjustment is required for the affected axis only.

The axis limits are arranged as follows:

retracted		           extended

────────────────────────────────────────────────────
|    |    |		       |    |    |
|    |    |------	prelimit	-------|    |    |
|    |-----------	operating limit	------------|    |
|----------------	emergency limit	-----------------|
|    |    |      		       |    |    |
|<-->|<-->|<-------	approx. 20 degr	------>|<-->|<-->|
|  a |  b |      		       | b  |  a |

Settings:

a	distance emergency limit - operating limit 	0.06 degr
b	distance operating limit - prelimit	0.06 degr

The adjustment procedure is as follows:

Warning!

If the instructions below are not strictly followed, the equipment may be damaged!

Therefore the adjustment work should be carried out by well experienced staff only!

Note:

All cam numbers given below are counted from inside, close to the rack gear (cam #1) to the outside (cam #6). Cams 5 and 6 are not used. The sense of rotation of the cams (cw/ccw) is given as seen from the end of the switch in direction to the rack gear.

1.	Switch the axis to be adjusted to "Local Only" mode at the drive cabinet.

2.	Deactivate softlimits by "misadjusting" the softlimit inside the PLC:
DB 50, DW152 = 2500	(GD up [10-2 degr])
DB 50, DW153 = -500	(GD down [10-2 degr])

resp.
DB 50, DW154 = 2500	(CH up [10-2 degr])
DB 50, DW155 = -500	(CH down [10-2 degr])

3.	Plug in Portable Control Unit at the appropriate PCU connection box.

4.	Remove cover of cam switch. The individual cams are visible now.

5.	Select Gregorian Dome (or Carriage House) axis at the PCU.

6.	Jumper prelimit and operating limit "up" in the cam switch by connecting +24V (grey wire) to the limit switch signal lines (green and yellow wires to cams 3 and 4, counted from inside).

7.	Make sure the emergency limit override is not activated!

8.	Move axis slowly into emergency limit up using the Portable Control Unit.
Note the axis position.

9.	Activate emergency limit override at the PCU connection box.

10.	Move axis slowly down to a position 0.04 degr below the position encountered in step 8.

Warning!

Use low speeds when operating the axis emergency limit override active!
Do not move the axis further into the limit switch!

11.	Stop axis after having reached a position 0.04 degr below the emergency limit.

12.	Remove the jumpers that have been installed in step 6 from the cam limit switch.

13.	Deactivate limit override.

14.	Set cam switch 4 ("limit up" - yellow wire) to the present position, i.e. the hump - moving clockwise - should touch the switch at this very position.

The cam can be adjusted by rotating it manually on the shaft. The activation of the switch can be heard by a soft "click".

The light "limit up" on the PCU should be illuminated now.

15.	Tighten the screw of cam 4.

16.	Verify proper operation of this limit by moving the axis into "down" direction by approx. 0.1 degr. Then reverse the movement and drive axis into the limit. It should be stopped automatically 0.04 degr (±0.005 degr) before the position noted in step 8.

Repeat steps 11 thru 16 if the distance between emergency limit and operating limit is outside the a.m. tolerance.

17.	Move axis to a position 0.04 degr below the operating limit "up".

18.	Set cam switch 3 ("prelimit up" - green wire) to the present position, i.e. the hump - moving clockwise - should touch the switch at this very position.

The cam can be adjusted by rotating it manually on the shaft. The activation of the switch can be heard by a soft "click".

The light "prelimit up" on the PCU should be illuminated now.

19.	Tighten the screw of cam 4.

20.	Verify proper operation of this limit by moving the axis into "down" direction by approx. 0.1 degr. Then reverse the movement and drive axis into the limit. It should be stopped automatically 0.04 degr (±0.005 degr) before the position noted in step 8.

Repeat steps 17 thru 20 if the distance between operating limit and prelimit is outside the a.m. tolerance.

21.	Repeat steps 6 thru 20 respectively for the "down" limits.

Please observe:

cam 2:	limit down	brown wire
cam 1:	prelimit down	white wire.

The cams for the "down" limits must be adjusted in such a way that the switch is activated by the hump moving in counterclockwise direction.

22.	Restore PLC softlimits by entereing the original values or by performing a cold restart. (All parameters will be set to their default values in the latter case.)

## 5.2.	Schmersal Mechanical Limit Switches

No adjustments required

Notes:

-	For all the emergency limit switches including the collision avoidance switch NC contacts are used (terminals 11 and 12 inside the switch)

-	The emergency limit switches for the Gregorian Dome are mounted on both sides of the uppermost truck.

-	For both Gregorian Dome and Carriage House the switch for limit "up" are mounted on the motor side of the truck. the switch for limit "down" is mounted on the opposite side.

# 6.	Vertex Drive Control System

The boards used within the DCS units are Vertex standard boards. Any deviations from the standard settings as well as jumper positions are listed hereafter.

## 6.1.	Drive Control System Azimuth

### 6.1.1.	Nominal Velocity Board 295.4

Slot in DCS: 4A1

velocity ramp	R 47	681 k 
	R 48	750 k
	R 52	499 k
	C3, C13	4.7 µF

hardware prelimit function	W 1	inserted
	W 2	inserted

speed zero threshold	R55, R56	50 mV

customer relay K14	X5	N/A

velocity ramp time 0 --> 10 V	R7
	slow (K10 not activated)		8 sec
	fast (K10 activated)		4 sec

### 6.1.2.	Actual Velocity Board 329.3

Slots in DCS: 5A1 thru 11A1 (7 pcs.)

#### 6.1.2.1.	Components

boards	boards
		5A1, 6A1	7A1, 
		8A1, 9A1	10A1, 11A1
───────────────────────────────────────────────────────────────

tacho adaption	R 1	0 	0   
	R 2	0 	0 
	R 5	0 	0 
	R 6	0 	0

tacho addition	R 13	130 k	61.9 k

speed zero threshold	R55, R56	N/A	50 mV

#### 6.1.2.2.	Tacho Adjustment

The values below are valid for the installed motor and amplifier configuration only.

Board 5A1:

1. 	Remove speed controller board 334.3 (12A1).

2.	Disconnect connector X4 at DCS rear panel.

3.	Either:

Discontinue PLC operation. Switch off PLC power. Remove EPROM. Switch PLC power on again. Perform an overall reset. Set output Q6.0 (load tacho 11) by the "Force Variable" function of the Step 5 software package.

Or:

Deactivate relay K2 by interrupting the line from PLC output Q6.1 to 5A1:16c. This can be done either by a switchable connector at X2 at the DCS rear panel (open wire X2:2) or by an extension card with individual jumpers for each pin.

4.	LED H2 must now be lit, H1 must be off at board 5A1.

5.	Connect a +2.360 VDC voltage between pins 18c and 32c of board 5A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

6.	Connect a DC Voltmeter between MP1 (at 5A1) and GND.

7.	Adjust voltage at MP1 to approx. 1.93 V using R51.

8.	Connect the DC Voltmeter to MP2.

9.	Adjust voltage at MP2 to approx. 1.93 V using R53.

10.	Connect DC Voltmeter to MP4. Voltage must be -5.00 V.

Repeat steps 6 thru 9 for "fine tuning" in order to reach -5.00 V at MP4. Voltages at MP1 and MP2 must be identical.

11.	Either:

Force Q6.0 (load tacho 11) to zero and Q6.1 (load tacho 12) to "1".

Or:

Activate relay K2 again by removing the interruption installed in step 3. Deactivate relay K1 by interrupting the line from PLC output Q6.0 to 5A1:16a. Pin at rear panel connector:  X2:1.

12.	LED H1 must now be lit, H2 must be off at board 5A1.

13.	Connect a +3.97 VDC voltage between pins 20c and 32c of board 5A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

14.	Connect a DC Voltmeter between MP1 (at 329.3) and GND.

15.	Adjust voltage at MP1 to approx. 1.930V using R52.

16.	Connect the DC Voltmeter to MP2.

17.	Adjust voltage at MP2 to approx. 1.930V using R50.

18.	Connect DC Voltmeter to MP4. Voltage must be -5.00 V.

Repeat steps 14 thru 18 for "fine tuning" in order to reach -5.00 V at MP4. Voltages at MP1 and MP2 must be identical.

19.	Remove all temporary settings, wirings etc. Re-install PLC Eprom if necessary and perform a cold restart. Re-install speed controller board 334.3 into slot 12A1. Reconnect X4 at DCS rear panel.

Note:

The input voltages to the actual velocity board are different for the two motors! This is because the velocity signal from the second motor is run through an additional inverter board. The input impedance of this inverter board is different from that of board 329.3. This has an influence on the scaling of the velocity signal coming out of the Kollmorgen amplifiers.

Board 6A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q6.2 / wire X2:4 (load tacho 41) and Q6.3 / wire X2:5 (load tacho 42) for steps 3 and 11.

Board 7A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q6.4 / wire X2:7 (load tacho 1) and Q6.5 / wire X2:8 (load tacho 4) for steps 3 and 11.

The voltage to be applied to the board is +5.00 V (steps 5 and 13). The voltage to be measured at MP4 is -5.00 V (steps 10 and 18). The voltage values measured at MP1 and MP2 (steps 7, 9, 15, 17) is not relevant (approx. 4 V), but the two readings must be identical.

Board 8A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q6.6 / wire X2:10 (load tacho 51) and Q6.7 / wire X2:11 (load tacho 52) for steps 3 and 11.

Board 9A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q7.0 / wire X2:13 (load tacho 81) and Q7.1 / wire X2:14 (load tacho 82) for steps 3 and 11.

Board 10A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q7.2 / wire X2:16 (load tacho 5) and Q7.3 / wire X2:17 (load tacho 8) for steps 3 and 11.

The voltage to be applied to the board is +5.00 V (steps 5 and 13). The voltage to be measured at MP4 is -5.00 V (steps 10 and 18). The voltage values measured at MP1 and MP2 (steps 7, 9, 15, 17) is not relevant (approx. 4 V), but the two readings must be identical.

Board 11A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q7.4 / wire X2:19 (load tacho 1/4) and Q7.5 / wire X2:20 (load tacho 5/8) for steps 3 and 11.

The voltage to be applied to the board is +5.00 V (steps 5 and 13). The voltage to be measured at MP4 is -5.00 V (steps 10 and 18). The voltage values measured at MP1 and MP2 (steps 7, 9, 15, 17) is not relevant (approx. 4 V), but the two readings must be identical.

#### 6.1.2.3.	Adjustment of Zero Speed Threshold

The zero speed feature is used at board 11A1 only. All boards including spares have already been correctly adjusted. The procedure is as follows:

1. 	Remove speed controller board 334.3 (slot 12A1).

2.	Disconnect X4 at DCS rear panel.

3.	Connect a +50 mV DC voltage between terminals 18c/20c and 32c of speed actual value board 11A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

4.	Turn R56 counterclockwise until LED H4 is off. After that turn R56 clockwise again until H4 is lit again.

6.	Swap the polarity of the 50 mV DC voltage (-50mV between 18c/20c and GND).

7.	Turn R55 counterclockwise until LED H4 is off. After that turn R55 clockwise again until H4 is lit again.

### 6.1.3.	Speed Controller Board 334.3

Slot in DCS: 12A1

#### 6.1.3.1.	Components

P-Controller	R 14	100 k
	R 16	18 k

I-Controller	C 14	3.3 µF
	R 17	100 k

n-Controller	R 43	100 k
(not used)	R 45	100 k
	R 71	
	C 13	10 µF

Jumper W1	O  open	   closed (GND)
Jumper W2	O  open	   closed (GND)
Jumper W3	O  open	   closed (GND)
Jumper W4	O  open	   closed (GND)
Jumper W5	O  open	   closed (GND)
Jumper W6	O  open	   closed (GND)
Jumper W7	O  open	   closed (GND)
Jumper W8	O  open	   closed (GND)
Jumper W9	   ab/cd	O    ad/cb
Jumper W10	   +15V	O    -15V
Jumper W11	O   +15V	    -15V

#### 6.1.3.2.	Bias torque adjustment

1.	Azimuth drive system should be operational (no failure reported) and not switched to Aux mode.

LED H1 at controller board should now be lit (torque bias activated).

2.	Connect voltmeter to MP3 at board 334.3.

3.	Adjust bias torque for drive 1 to 0.25 V using R4.

4.	Connect voltmeter to MP4 at board 334.3.

5.	Adjust bias torque for drive 2 to 0.25 V using R5.

### 6.1.4.	Universal Amplifier Board 421.0

Slots in DCS: 13A1 thru 16A1 (4 pcs.)

#### 6.1.4.1.	Components

boards	boards
		13A1, 14A1	15A1, 16A1
───────────────────────────────────────────────────────────────

differential velocity gain	R 101, 201, 301, 401	10 k	 
	R 102, 202, 302, 402	10 k	 
	R 103, 203, 303, 403	27 k (see note below)
	R 104, 204, 304, 404	6.8 k
	W 101, 201, 301, 401	inserted
	W 102, 202, 303, 403	inserted
	W 103, 203, 303, 403	ad - cb

feedarm bending comp. gain	R 102, 202, 303, 403	10 k
	R 501, 502	10 k
	R 503	12 k
	C 501, 502	0 (jumper)

sum points	R 101, 201, 301, 401		10 k	 
	R 102, 202, 302, 402		10 k
	R 103, 203, 303, 403		10 k
	R 104, 204, 304, 404		10 k
	R 501, 502, 503		10 k
	C 501, 502		0 (jumper)
	W 101, 201, 301, 401		inserted
	W 102, 202, 303, 403		inserted
	W 103, 303		ad -cb
	W 203, 403		ab -cd

Note - R 103/203/303/403 on boards 13A1 and 14A1:

The resistors have to be wired "across each other", see table below:

left end of resistor 	R 103 goes to right end of 	R 303
	R 203	R 403
	R 303	R 103
	R 403	R 203.

## 6.2.	Drive Control System Gregorian Dome

### 6.2.1.	Nominal Velocity Board 295.4

Slot in DCS: 4A1

velocity ramp	R 47	243 k 
	R 48	300 k
	R 52	499 k
	C3, C13	4.7 µF

hardware prelimit function	W 1	inserted
	W 2	inserted

speed zero threshold	R55, R56	50 mV

customer relay K14	X5	N/A

velocity ramp time 0 --> 10 V	R7
	slow (K10 not activated)		3 sec
	fast (K10 activated)		1.5 sec

### 6.2.2.	Actual Velocity Board 329.3

Slots in DCS: 5A1 thru 11A1 (7 pcs.)

#### 6.2.2.1.	Components

boards	boards
		5A1, 6A1	7A1, 
		8A1, 9A1	10A1, 11A1
───────────────────────────────────────────────────────────────

tacho adaption	R 1	0 	0   
	R 2	0 	0 
	R 5	0 	0 
	R 6	0 	0

tacho addition	R 13	150 k	61.9 k

speed zero threshold	R55, R56	N/A	50 mV

#### 6.2.2.2.	Tacho Adjustment

The values below are valid for the installed motor and amplifier configuration only.

Board 5A1:

1. 	Remove speed controller board 334.3 (12A1).

2.	Disconnect connector X4 at DCS rear panel.

3.	Either:

Discontinue PLC operation. Switch off PLC power. Remove EPROM. Switch PLC power on again. Perform an overall reset. Set output Q14.0 (load tacho 11) by the "Force Variable" function of the Step 5 software package.

Or:

Deactivate relay K2 by interrupting the line from PLC output Q14.1 to 5A1:16c. This can be done either by a switchable connector at X2 at the DCS rear panel (open wire X2:2) or by an extension card with individual jumpers for each pin.

4.	LED H2 must now be lit, H1 must be off at board 5A1.

5.	Connect a +4.270 VDC voltage between pins 18c and 32c of board 5A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

6.	Connect a DC Voltmeter between MP1 (at 5A1) and GND.

7.	Adjust voltage at MP1 to approx. 3.33 V using R51.

8.	Connect the DC Voltmeter to MP2.

9.	Adjust voltage at MP2 to approx. 3.33 V using R53.

10.	Connect DC Voltmeter to MP4. Voltage must be -10.000 V.

Repeat steps 6 thru 9 for "fine tuning" in order to reach -10.000 V at MP4. Voltages at MP1 and MP2 must be identical.

11.	Either:

Force Q14.0 (load tacho 11) to zero and Q14.1 (load tacho 12) to "1".

Or:

Activate relay K2 again by removing the interruption installed in step 3. Deactivate relay K1 by interrupting the line from PLC output Q14.0 to 5A1:16a. Pin at rear panel connector:  X2:1.

12.	LED H1 must now be lit, H2 must be off at board 5A1.

13.	Connect a +4.270 VDC voltage between pins 20c and 32c of board 5A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

14.	Connect a DC Voltmeter between MP1 (at 329.3) and GND.

15.	Adjust voltage at MP1 to approx. 3.330V using R52.

16.	Connect the DC Voltmeter to MP2.

17.	Adjust voltage at MP2 to approx. 3.330V using R50.

18.	Connect DC Voltmeter to MP4. Voltage must be -10.000 V.

Repeat steps 14 thru 18 for "fine tuning" in order to reach -10.000 V at MP4. Voltages at MP1 and MP2 must be identical.

19.	Remove all temporary settings, wirings etc. Re-install PLC Eprom if necessary and perform a cold restart. Re-install speed controller board 334.3 into slot 12A1. Reconnect X4 at DCS rear panel.

Board 6A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q14.2 / wire X2:4 (load tacho 21) and Q14.3 / wire X2:5 (load tacho 22) for steps 3 and 11.

Board 7A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q14.4 / wire X2:7 (load tacho 1) and Q14.5 / wire X2:8 (load tacho 2) for steps 3 and 11.

The voltage to be applied to the board is +5.000 V (steps 5 and 13). The voltage to be measured at MP4 also is -5.000 V (steps 10 and 18). The voltage values measured at MP1 and MP2 (steps 7, 9, 15, 17) are not relevant (approx. 4 V), but the two readings must be identical.

Board 8A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q14.6 / wire X2:10 (load tacho 31) and Q14.7 / wire X2:11 (load tacho 32) for steps 3 and 11.

Board 9A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q15.0 / wire X2:13 (load tacho 41) and Q15.1 / wire X2:14 (load tacho 42) for steps 3 and 11.

Board 10A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q15.2 / wire X2:16 (load tacho 3) and Q15.3 / wire X2:17 (load tacho 4) for steps 3 and 11.

The voltage to be applied to the board is +5.000 V (steps 5 and 13). The voltage to be measured at MP4 is -5.000 V (steps 10 and 18). The voltage values measured at MP1 and MP2 (steps 7, 9, 15, 17) are not relevant (approx. 4 V), but the two readings must be identical.

Board 11A1:

Same procedure as described above for board 5A1. However, use PLC outputs Q15.4 / wire X2:19 (load tacho 1/2) and Q15.5 / wire X2:20 (load tacho 3/4) for steps 3 and 11.

The voltage to be applied to the board is +5.000 V (steps 5 and 13). The voltage to be measured at MP4 is -5.000 V (steps 10 and 18). The voltage values measured at MP1 and MP2 (steps 7, 9, 15, 17) are not relevant (approx. 4 V), but the two readings must be identical.

#### 6.2.2.3.	Adjustment of Zero Speed Threshold

The zero speed feature is used at board 11A1 only. All boards including spares have already been correctly adjusted. The procedure is as follows:

1. 	Remove speed controller board 334.3 (slot 12A1).

2.	Disconnect X4 at DCS rear panel.

3.	Connect a +50 mV DC voltage between terminals 18c/20c and 32c of speed actual value board 11A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

4.	Turn R56 counterclockwise until LED H4 is off. After that turn R56 clockwise again until H4 is lit again.

6.	Swap the polarity of the 50 mV DC voltage (-50mV between 18c/20c and GND).

7.	Turn R55 counterclockwise until LED H4 is off. After that turn R55 clockwise again until H4 is lit again.

### 6.2.3.	Speed Controller Board 334.3

Slot in DCS: 12A1

#### 6.2.3.1.	Components

P-Controller	R 14	100 k
	R 16	20 k

I-Controller	C 14	3.3 µF
	R 17	332 k

n-Controller	R 43	100 k
	R 45	100 k
	R 71	
	C 13	10 µF

Jumper W1	O  open	   closed (GND)
Jumper W2	O  open	   closed (GND)
Jumper W3	O  open	   closed (GND)
Jumper W4	O  open	   closed (GND)
Jumper W5	O  open	   closed (GND)
Jumper W6	O  open	   closed (GND)
Jumper W7	O  open	   closed (GND)
Jumper W8	O  open	   closed (GND)
Jumper W9	   ab/cd	O    ad/cb
Jumper W10	   +15V	O    -15V
Jumper W11	O   +15V	    -15V

#### 6.2.3.2.	Torque Bias Adjustment

The torque bias feature on this board is not used. The torque bias is fed directly from an analog PLC output to the amplifier board 15A1 (see below).

### 6.2.4.	Universal Amplifier Board 421.0

Slots in DCS: 13A1 thru 16A1 (4 pcs.)

#### 6.2.4.1.	Components

boards	boards
		13A1, 14A1	15A1, 16A1
───────────────────────────────────────────────────────────────

differential velocity gain	R 101, 201, 301, 401	10 k	 
	R 102, 202, 302, 402	10 k
	R 103, 203, 303, 403	39 k (see note below)
	R 104, 204, 304, 404	5.6 k
	R 501	0 (jumper) (13A1 only)
	R 502	10 k (13A1 only)
	R 503	8.2 k (13A1 only)
	C 501, 502	0 (jumper)
	W 101, 201, 301, 401	inserted
	W 102, 202, 303, 403	inserted
	W 103, 203, 303, 403	ad -cb

sum points	R 101, 201, 301, 401		10 k	 
	R 102, 202, 302, 402		10 k
	R 103, 203, 303, 403		10 k
	R 104, 204, 304, 404		10 k
	R 501, 502		10 k
	C 501, 502		0 (jumper)
	W 101, 201, 301, 401		inserted
	W 102, 202, 303, 403		inserted
	W 103, 203, 303, 403		ad -cb

Note - R 103/203/303/403 on boards 13A1 and 14A1:

The resistors have to be wired "across each other", see table below:

left end of resistor 	R 103 goes to right end of 	R 303
	R 203	R 403
	R 303	R 103
	R 403	R 203.

## 6.3.	Drive Control System Carriage House

### 6.3.1.	Nominal Velocity Board 295.4

Slot in DCS: 4A1

velocity ramp	R 47	243 k 
	R 48	300 k
	R 52	499 k
	C3, C13	4.7 µF

hardware prelimit function	W 1	inserted
	W 2	inserted

speed zero threshold	R55, R56	50 mV

customer relay K14	X5	N/A

velocity ramp time 0 --> 10 V	R7
	slow (K10 not activated)		3 sec
	fast (K10 activated)		1.5 sec

### 6.3.2.	Actual Velocity Board 329.3

Slot in DCS: 11A1

#### 6.3.2.1.	Components

tacho adaption	R 1	0   
	R 2	0 
	R 5	0 
	R 6	0

tacho addition	R 13	150 k

speed zero threshold	R55, R56	50 mV

#### 6.3.2.2.	Tacho Adjustment

The values below are valid for the installed motor and amplifier configuration only.

1. 	Remove speed controller board 334.3 (12A1).

2.	Disconnect connector X4 at DCS rear panel.

3.	Either:

Discontinue PLC operation. Switch off PLC power. Remove EPROM. Switch PLC power on again. Perform an overall reset. Set output Q18.0 (load tacho 11) by the "Force Variable" function of the Step 5 software package.

Or:

Deactivate relay K2 by interrupting the line from PLC output Q18.1 to 11A1:16c. This can be done either by a switchable connector at X2 at the DCS rear panel (open wire X1:20) or by an extension card with individual jumpers for each pin.

4.	LED H2 must now be lit, H1 must be off at board 11A1.

5.	Connect a +4.270 VDC voltage between pins 18c and 32c of board 11A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

6.	Connect a DC Voltmeter between MP1 (at 11A1) and GND.

7.	Adjust voltage at MP1 to approx. 3.33 V using R51.

8.	Connect the DC Voltmeter to MP2.

9.	Adjust voltage at MP2 to approx. 3.33 V using R53.

10.	Connect DC Voltmeter to MP4. Voltage must be -10.000 V.

Repeat steps 6 thru 9 for "fine tuning" in order to reach -10.000 V at MP4. Voltages at MP1 and MP2 must be identical.

11.	Either:

Force Q18.0 (load tacho 11) to zero and Q18.1 (load tacho 12) to "1".

Or:

Activate relay K2 again by removing the interruption installed in step 3. Deactivate relay K1 by interrupting the line from PLC output Q14.0 to 5A1:16a. Pin at rear panel connector:  X1:19.

12.	LED H1 must now be lit, H2 must be off at board 11A1.

13.	Connect a +4.270 VDC voltage between pins 20c and 32c of board 11A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

14.	Connect a DC Voltmeter between MP1 (at 329.3) and GND.

15.	Adjust voltage at MP1 to approx. 3.330V using R52.

16.	Connect the DC Voltmeter to MP2.

17.	Adjust voltage at MP2 to approx. 3.330V using R50.

18.	Connect DC Voltmeter to MP4. Voltage must be -10.000 V.

Repeat steps 14 thru 18 for "fine tuning" in order to reach -10.000 V at MP4. Voltages at MP1 and MP2 must be identical.

19.	Remove all temporary settings, wirings etc. Re-install PLC Eprom if necessary and perform a cold restart. Re-install speed controller board 334.3 into slot 12A1. Reconnect X4 at DCS rear panel.

#### 6.3.2.3.	Adjustment of Zero Speed Threshold

1. 	Remove speed controller board 334.3 (slot 12A1).

2.	Disconnect X4 at DCS rear panel.

3.	Connect a +50 mV DC voltage between terminals 18c/20c and 32c of speed actual value board 11A1.
(Instead of terminal 32c [GND] the black socket on the 329.3 front panel may be used.)

4.	Turn R56 counterclockwise until LED H4 is off. After that turn R56 clockwise again until H4 is lit again.

6.	Swap the polarity of the 50 mV DC voltage (-50mV between 18c/20c and GND).

7.	Turn R55 counterclockwise until LED H4 is off. After that turn R55 clockwise again until H4 is lit again.

### 6.3.3.	Speed Controller Board 334.3

Slot in DCS: 12A1

#### 6.3.3.1.	Components

P-Controller	R 14	100 k
	R 16	30 k

I-Controller	C 14	3.3 µF
	R 17	332 k

n-Controller	R 43	100 k
	R 45	22 k
	R 71	
	C 13	10 µF

Jumper W1	O  open	   closed (GND)
Jumper W2	O  open	   closed (GND)
Jumper W3	O  open	   closed (GND)
Jumper W4	O  open	   closed (GND)
Jumper W5	O  open	   closed (GND)
Jumper W6	O  open	   closed (GND)
Jumper W7	O  open	   closed (GND)
Jumper W8	O  open	   closed (GND)
Jumper W9	O   ab/cd	    ad/cb
Jumper W10	   +15V	O    -15V
Jumper W11	O   +15V	    -15V

#### 6.3.3.2.	Torque Bias Adjustment

The torque bias feature on this board is not used. The torque bias is fed directly from an analog PLC output to the inputs 16c and 18c of board 334.3.

# 7.	Uninterruptable Power Supply

no adjustment required

# 8.	Switchgear Inside Drive Cabinet

## 8.1.	Voltage Supervision Relay Dold BA 9054

The voltage supervision relays (circuit diagram labels +Az/GD/CH - 02D02 and 03D02) check the DC bus voltage for overvoltage. The DC bus is the output of the Kollmorgen power supply modules and the power input for the servo amplifiers.

Setting of all relays:

Voltage	0.70 (equals 360 V)
Hysteresis	0.98

## 8.2.	Current Supervision Relay Pilz P1IK

The current supervision relays (circuit diagram labels +PD - 27CR0*) are used for measuring the total current through one group of brakes. If adjusted as indicated below failure of one individual brake will be detected.

If a motor is completely removed it might be necessary to readjust the related brake current relay.

Settings:

Azimuth and Gregorian Dome (relays +PD-27CR01, 27CR02, 27CR03, 27CR04):

Current (big scale) 	4.2
Hysteresis (small scale)	0.95

Carriage House (relay +PD-27CR05):

Current (big scale) 	2.0
Hysteresis (small scale)	0.95

## 8.3	Schiele Overvoltage Protection Relay

The overvoltage protection relay (circuit diagram label +PD - 21D01) check the mains voltage for overvoltage and undervoltage.

Allowed voltage range:	480 V ± 10%, i.e. 432 ... 528 V.

Settings:

Overvoltage 	530 V
Undervoltage 	430 V
Function 	 (delayed release)
time delay for recovery	5 sec

# Footnotes

11A1 only (not used on 7A1, 10A1)

board 13A1 only; not used on board 14A1

11A1 only (not used on 7A1, 10A1)

11A1 only (not used on 7A1, 10A1)